## Default performances
Information Sheet for Specified Systems | [5 empty] | IS SS Revision 1: 27/11/2019
Building consent |  |  |  | Construction and Code Compliance
Specified System | System description | Performance for design & installation | Building consent | Performance for Inspection and Maintenance | Recording & responsibility | Code Compliance Certification (CCC documents)
SS 1 Automatic systems for fire suppression | [Select] Type 6 Automatic fire sprinkler system manual call points Type 7 Automatic fire sprinkler system with smoke detection and manual call points Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | Designed and installed to NZS4541:2013 Automatic fire sprinklers systems and NZS 4512:2010 Fire Detection and Alarm Systems in buildings | Application Form 27 Application for compliance schedule Fire Design specifying performance for sprinkler design & installation Building Consent Form 5 SS 01 Automatic systems for fire suppression [insert] to NZS4541:2013 Automatic fire sprinklers systems and NZS 4512:2010 Fire Detection and Alarm Systems in buildings Construction Documentation PS 3 & supporting documentation from sprinkler system installer Certificate of Compliance from an accredited Sprinkler System Certifier PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Automatic systems for fire suppression require regular inspections and testing to ensure the systems will operate as required by the performance standard in the event of a fire. Inspections and maintenance to NZS 4541:2013 Automatic fire sprinklers systems | Monthly - IQP Annually IQP | Sprinkler system installer provides PS 3 and all commissioning test data, certifying the designed is installed and commissioned is in accordance with the approved building consent documentation Accredited Sprinkler System Certifier (SSC) to provide a Certificate of Compliance Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation Make, model and location (throughout building) from certificate As built drawings.
SS 2 Automatic or manual emergency warning systems | [Select] Type 2 – manual alarm with manual call points Type 3 – automatic fire alarm with heat detection and manual call points Type 4 – automatic fire alarm system with smoke detection and manual call points Type 5 – automatic fire alarm system with enhanced smoke detection and manual call points Interfaced with: SS1 Fire suppression system SS3/1 Auto doors SS3/2 Access controlled doors SS3/3 Fire/smoke doors SS5 Escape route pressurization SS8/1 Lifts SS8/3 Escalator SS9 Mechanical Ventilation SS13/1 Mechanical Smoke Control SS13/2 Natural Smoke Control SS13/3 Smoke Curtain | [Select] (Type 2 , 3 & 4) NZS 4512:2010 Fire Detection and Alarm Systems in buildings (Type 5) NZS 4512:2010 Fire Detection and Alarm Systems in buildings and F7/AS1 Warning Systems Acceptable Solution | Application Form 27 Application for compliance schedule Fire Design specifying performance for alarm design & installation Building Consent SS 02 Automatic or manual emergency warning systems. Type [select] to [select] PS 3 & supporting documentation from alarm system installer Certificate of completion from accredited body PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Inspections Emergency warning system require regular inspection and testing to ensure the system will operate as required by the performance standard in the event of fire or other danger Inspections and Maintenance to NZS 4512:2010 Fire Detection and Alarm Systems in buildings Parts 1 - 5. (Interface with other specified systems NZS 4512:2010 Section 603 - Annual checks and tests) | Monthly - IQP Annually - IQP | (if on Building Consent documents) Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation Fire alarm installer provides PS3 certifying the designed, installed and commissioned is in accordance with the approved building consent documentation. Accredited body provides Certificate of Completion Make, model and location (from certificate) As built drawings
SS 3 Electromagnetic or Automatic doors or windows | SS 3/1 Automatic Doors [Select] Automatic sliding door Automatic revolving door Automatic sliding door interfaced with emergency warning system Automatic revolving door interfaced with emergency warning system | [Select] AS 5007:2007 Powered doors for pedestrian access and egress NZS 4239:1993 Automatic sliding door assemblies | Application Form 27 Application for compliance schedule Manufacturers literature for selected door(s) specifying standard tested to. Building Consent SS 03/1 Automatic door [select] to [select] | Automatic doors require regular inspection and testing to ensure the system will operate as required by the performance standard below to ensure occupants are not prevented from leaving the building in the event of an emergency and people with disabilities are able to gain access to the internal space of the building. Inspections & maintenance as listed in Compliance Schedule Handbook for SS 3/1 ( B.5-B.26 & C1 – C.5) | [Select] Crowd Occupancies Daily - Owner (if >1 exit & >1 level) 3 Monthly - Owner Annually - IQP Other Occupancies Monthly - Owner Annually - IQP | Make, model and location(s) (from Building Consent documents) Assess if crowd occupancy (Fire report)
| SS 3/2 Access Controlled Doors [Select] Swipe card access Proximity sensor access Key pad access Delayed egress Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | [Select] Specific design to meet the requirements of C/AS2 2019 Amendment 1 paragraphs 3.15.2 and 3.15.7 Code of Practice for Electro Mechanical Controlled Locking Devices on egress doors. Association of Building Compliance (ABC) August 2018 | Application Form 27 Application for compliance schedule Manufacturers literature for selected door(s) specifying standard tested to. Building Consent Form 5 SS 03/2 Access Controlled Door [select] to [select] | Access-controlled doors require regular inspections to ensure occupants are not prevented from leaving the building are able to leave the building without the use of swipe cards, keys or other security devices in the event of an emergency. Inspections & maintenance as listed in Compliance Schedule Handbook for SS 3/2 Where the door control system is inter-faced to the fire alarm system this needs to be checked at the same time. | [Select] Crowd Occupancies Daily - Owner (if >1 exit & >1 level) Monthly - IQP Annually - IQP Other Occupancies Monthly - Owner Annually - IQP | Make, model and location(s) (from Building Consent documents) Assess if crowd occupancy and door interfaced (Fire report)
| SS03/3 Interfaced fire or smoke doors or windows (designed to open or close on activation of the building emergency warning system or detection device) [Select] Fire or smoke door designed to open or close on the activation of the building emergency warning system or detection device Fire or smoke window designed to open or close on the activation of the building emergency warning system or detection device Electromagnetic held-open door Fusible link release type Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | Specific design to meet the requirements of C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH paragraphs 3.15.9 and 3.15.10 | Application Form 27 Application for compliance schedule Fire repot & drawings specifying performance and showing locations Building Consent Form 5 SS 3/3 Interfaced fire or smoke doors or windows [select] to Specific design to meet the requirements of C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH paragraphs 3.15.9 and 3.15.10 | Interfaced fire and smoke doors or window require regular inspections to ensure they operate as required by the performance standards in event of fire. Inspections & maintenance as listed in Compliance Schedule Handbook for SS 3/3 | [Select] Crowd Occupancies Daily - Owner (if >1 exit & >1 level) Monthly - IQP Annually - IQP Other Occupancies Monthly - Owner Annually - IQP | Make, model and location(s) (from Building Consent documents) Assess if crowd occupancy (Fire report)
SS 4 Emergency lighting systems | [Select] Emergency lighting system on escape route Emergency lighting installed for identification of the exit ways of a building (illuminated exit signs) Change of levels | AS / NZS 2293:2018 Emergency lighting and exit signs for buildings. Part 1 System design, installation and operation & Part 3 Emergency luminaires and exit signs | Application Form 27 Application for compliance schedule Producer Statement Design (PS1) for F6 (Emergency Lighting Design) Building Consent Form 5 SS 4 Emergency lighting systems for [select] to AS / NZS 2293.1:2018 Emergency lighting and exit signs for buildings. Part 1 System design, installation and operation & Part 3 Emergency luminaires and exit signs Construction documentation PS3 and supporting documents form emergency lighting installer PS3 and supporting documents from illuminated exit sign installer | Emergency lighting systems require regular inspection and testing to ensure effective operation for the required duration in the event of failure of the general lighting system Inspections and maintenance to AS/NZS 2293.2:2019 Emergency lighting and exit signs for building Routine service and maintenance | Monthly - IQP Annually - IQP | Emergency lighting installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation Illuminated exit signs installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation Reference BC document where compliance shown (e.g. As documented on fire drawing number and / or date ) on CS
SS5 Escape route pressurisation systems | [Select] Corridor pressurisation system Stairwell pressurisation system Lift shaft pressurisation system Interfaced with SS2 - Automatic or manual emergency warning systems for fire or other dangers | AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings | Application Form 27 Application for compliance schedule Fire Design referencing performance for design and installation Building Consent Form 5 SS 5 Escape route pressurisation systems [select] to AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings Construction documentation PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Escape route pressurisation systems require annual inspection and testing to ensure the system will operate as required by the performance standard in the event of a fire. The annual test to include -a test of the operation of any interface with the emergency warning system for fire. Inspections an maintenance to AS 1851:2012 Route service of fire protection systems and equipment | Monthly - IQP Annually - IQP | Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation
SS 6 Riser Mains | [Select] Dry Riser Charged Riser Underground fire hydrant | [Select] NZS 4510:2008 Fire hydrant systems for buildings NZS 4522:2010 Underground fire hydrants | Application Form 27 Application for compliance schedule Fire Design referencing performance for design and installation Building Consent Form 5 SS 6 Riser Main [select] to [select] Construction documentation PS4 from CPEngineer certifying system will be installed in accordance with approved consent documents (discuss with h & c currently only have passive fire PS4) | Riser mains for use by fire services require annual, two yearly and five yearly inspections and testing to ensure the system will operate as required by the performance standard in the event of a fire. | Annually - IQP | Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation
SS 7 Automatic back-flow preventers (connected to potable water supply and not owned by the NUO) | [Select] Reduced Pressure Zone devices Double Check Valve Assemblies Pressure Type Vacuum Breakers Atmospheric Vacuum Breakers Sprinkler System | G12/AS1 Water Supplies Acceptable Solution amendment 12. Sections 3.6.2 - 3.6.4 | Application Form 27 Application for compliance schedule Documentation showing compliance with G12 including make, model and location Building Consent Form 5 SS 7 Automatic back-flow preventers [select] to G12/AS1 Water Supplies Acceptable Solution amendment 12. Sections 3.6.2 - 3.6.4 | Automatic backflow preventers require annual testing and inspection to ensure they provide protection to the drinking water supply. Automatic backflow preventer to be inspected and tested after repair or replacement. Inspections and maintenance to AS/NZS 2845.3:1993/2010 and NZ Industry Standard – Field testing of backflow prevention devices and verification of air gaps 2011 | Annually - IQP | Make, model and location description (from Building Consent documents)
SS 8 Lift, escalators, travellators, or other systems for moving people or goods within buildings | SS 8/1 Passenger-carrying lifts [Select if interfaced with SS2] Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | [Select] Schindler methodology of Code Mark Certificate Number AQ-070715-CMNZ (Rev. 3 - June 16) EN 81-20:2014 Safety rules for the construction and installation of lifts. Lifts for the transport of persons and goods. | Application Form 27 Application for compliance schedule Documentation showing compliance with D2 including make, model and location Schindler only - CodeMark - Maintenance schedule from Schindler Building Consent Form 5 SS 8/1 Passenger lift [select if interfaced] to [select] Construction documentation PS3 and supporting documentation from lift installer | Passenger carrying lifts require six-monthly and annual inspection and testing to ensure they operate as required by the performance standard. [Select] (if installed to CodeMark) Inspection and maintenance schedule from Schindler (submitted with the building consent) (If installed to EN 81) Inspections and maintenance to EN 81 Clause D.2 and MBIE compliance schedule handbook checklists for passenger carrying lifts complying with D2/AS1 (If installed to NZS 4332 Inspections and maintenance to MBIE compliance schedule handbook checklists for passenger carrying lifts complying with D2/AS1 | Monthly - IQP Annually - IQP | Make, model and location description (from Building Consent documents) (Schindler only) - Schindler declaration provided to confirm installation is in accordance with the Schindler methodology specified in CodeMark Lift installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation
| SS 8/2 Platform, Low Speed & Service Lifts [Select] Platform lift Dumb waiter Good hoist Vehicle stacking system Stage lift Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | NZS 4334:2012 Platform lifts and low-speed lifts | Application Form 27 Application for compliance schedule Documentation showing compliance with D2 including make, model and location Building Consent Form 5 SS 8/2 Platform, Low Speed & Service Lifts [select] to NZS 4334:2012 Platform lifts and low-speed lifts Construction documentation PS3 and supporting documentation from lift installer | Service lifts require six-monthly and annual inspection and testing to ensure they operate as required by the performance standard and to ensure loading and unloading provisions are safe. Inspections and maintenance to NZS 4334:2012 Platform lifts and low-speed lifts Appendix A | Monthly - IQP Annually - IQP | Make, model and location description (from Building Consent documents) Lift installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation
| SS 8/3 Escalators and Moving Walks [Select] Escalator Moving horizontal walkway Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | EN 115.1:2008 Safety of escalators and moving walks | Application Form 27 Application for compliance schedule Documentation showing compliance with D2 including make, model and location Building Consent Form 5 SS 8/3 Escalators and Moving Walks [select] to EN 115.1:2008 Safety of escalators and moving walks Construction documentation PS3 and supporting documentation from lift installer | Escalators and moving walks require six-monthly and annual inspection and testing to ensure they operate as required by the performance standard. Inspections and maintenance to EN 115.1:2008 Safety of escalators and moving walks - clause 7.4 | Monthly - IQP Annually - IQP | Lift installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation
SS 9 Mechanical ventilation or air conditioning systems | [Select] Extract system serving multiple units or facilities System required to function in smoke management or smoke clearance mode during a fire Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | AS 1668.2:2012 The use of mechanical ventilation and air-conditioning in buildings Part 2 Ventilation design for indoor-air contaminant control Amendments: 1 & 2 | Application Form 27 Application for compliance schedule PS1 - G4 and drawings for HAVC Building Consent Form 5 SS 9 Mechanical ventilation [Select] to AS 1668.2:2002 The use of mechanical ventilation and air-conditioning in buildings Part 2 Ventilation design for indoor-air contaminant control Amendments: 1 & 2 Construction documentation PS3 and supporting documents from HVAC installer | Mechanical ventilation and air conditioning systems including any of its interfaces with other specified system require monthly, three-monthly and annual inspections to ensure they operate as required by the performance standard and to ensure preservation of any inbuilt safety features. Inspections and maintenance to AS 1668.2:2002 The use of mechanical ventilation and air-conditioning in buildings Part 2 Ventilation design for indoor-air contaminant control | Daily - Owner 3 Monthly - Owner 6 Monthly - Owner Annually - IQP | HVAC installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation. Reference BC document where compliance shown (e.g. As documented on mechanical drawing number and date ) on CS
SS 10 Building Maintenance Units | Gantry that is secured to the side of the building by a track using a wheeled trolley for positioning | BS 6037-1:2017 Planning, design, installation and use of permanently installed access equipment. Code of practice. Suspended access equipment | Application Form 27 Application for compliance schedule Full documentation supported by PS1 for structural design Building Consent Form 5 SS 10 Building Maintenance Units Gantry that is secured to the side of the building by a track using a wheeled trolley for positioning to BS 6037-1:2017 Planning, design, installation and use of permanently installed access equipment. Code of practice. Suspended access equipment Construction documentation PS4 and Structural engineer | Building maintenance units require monthly, six-monthly and annual inspection and testing to ensure they operate as required by the performance standard. Inspections and maintenance to BS 6037-1:2017 Planning, design, installation and use of permanently installed access equipment. Code of practice. Suspended access equipment | Monthly - IQP 6 Monthly - IQP Annually - IQP | Structural Engineer supply PS4 certifying systems installed in accordance with consent documentation Reference BC document where compliance shown (e.g. As documented on structural drawing number and date ) on CS
SS 11 Laboratory fume cupboards | Ducted fumed cupboard for laboratory use | AS/NZS 2243.8:2014 Safety in laboratories Part 8: Fume cupboards | Application Form 27 Application for compliance schedule Full design documentation including reference to standard. Building Consent Form 5 SS 11 Laboratory fume cupboards Ducted fumed cupboard for laboratory use to AS/NZS 2243.8:2014 Safety in laboratories Part 8: Fume cupboards | Laboratory fume cupboards require regular inspections and testing to ensure they operate as required by the performance standard. Inspections and maintenance to AS/NZS 2243.8:2014 Safety in laboratories Part 8: Fume cupboards | Monthly - IQP Annually - IQP | Make Model and Location from BC documents
SS 12 Audio Loops or other assistive listening systems | SS 12/1 Audio Loops | NZS 4121:2001 Design for access and mobility - Buildings and associated facilities. Appendix H | Application Form 27 Application for compliance schedule System technical literature referencing standard Building Consent Form 5 SS 12/1 Audio Loops to NZS 4121:2001 Design for access and mobility - Buildings and associated facilities. Appendix H Construction documentation PS3 and supporting documents from installer | Audio loops require regular inspection to ensure they operate as required by the performance standard Inspections and maintenance to MBIE compliance schedule handbook for SS12/1 (B.1 - B.3) | 6 Monthly - IQP Annually - IQP | Audio loop installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation.
| SS 12/2 FM radio frequency systems and infrared beam transmission systems | NZS 4121:2001 Design for access and mobility - Buildings and associated facilities. Appendix H | Application Form 27 Application for compliance schedule System technical literature referencing standard Building Consent Form 5 SS 12/2 FM radio frequency systems and infrared beam transmission systems Audio Loops to NZS 4121:2001 Design for access and mobility - Buildings and associated facilities. Appendix H Construction documentation PS3 and supporting documents from installer | FM radio frequency systems and IR beam transmission systems are required to be inspected regularly to ensure they operate as required by the performance standard. Inspections an maintenance to MBIE compliance schedule handbook for SS12/2 (B.1 - B.5.6) | 6 Monthly - IQP Annually - IQP | FM radio system installer provides commissioning test data and PS3 certifying installed in accordance with the approved building consent documentation.
SS 13 Smoke control systems | SS13/1 Mechanical Smoke Control [Select] Dedicated smoke exhaust Dedicated smoke control Purge system Zone pressurization (pressurization other then escape route pressurization) Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | Designed and installed to AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings. Part 1 Fire and smoke control in multi-compartment buildings | Application Form 27 Application for compliance schedule Fire report specifying system and performance standard Building Consent Form 5 SS 13/1 Mechanical Smoke Control [Select] to Designed and installed to AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings. Part 1 Fire and smoke control in multi-compartment buildings Construction documentation PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Mechanical smoke ventilation systems require regular inspection and testing to ensure they operate as required by the performance standard in the event of a fire. Inspections an maintenance to AS 1851:2012 Routine service of fire protection systems and equipment | Monthly - IQP Annually - IQP | Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation
| SS13/2 Natural Smoke Control [Select] Natural smoke ventilator which is designed to open automatically after the outbreak of fire Smoke reservoir specifically design within a building to retain or collect a thermally buoyant smoke layer in the event of a fire Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | Designed and installed to AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings. Part 1 Fire and smoke control in multi-compartment buildings | Application Form 27 Application for compliance schedule Fire report specifying system and performance standard Form 5 SS 13/12 Natural Smoke Control [Select] to AS/NZS 1668.1:2015 The use of ventilation and air conditioning in buildings. Part 1 Fire and smoke control in multi-compartment buildings Construction documentation PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Natural smoke control systems require regular inspection and testing to ensure they operate as required by the performance standard in the event of a fire. Inspections an maintenance to AS 1851:2012 Routine service of fire protection systems and equipment | Monthly - Owner 6 Monthly - IQP Annually - IQP | Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation
| SS13/3 Smoke Curtains [Select] Automatic smoke curtain – brand/name, type and location Interfaced with: SS2 - Automatic or manual emergency warning systems for fire or other dangers | Designed and installed BS EN 12101 Smoke and heat control systems Part 1: 2005 Specification for smoke barriers | Application Form 27 Application for compliance schedule Full technical literature including reference to standard Building Consent Form 5 SS 13/3 Smoke Curtains [Select] to BS EN 12101 Smoke and heat control systems Part 1: 2005 Specification for smoke barriers Construction documentation PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Mechanical smoke ventilation systems require regular inspection and testing to ensure they operate as required by the performance standard in the event of a fire. Inspections an maintenance to AS 1851:2012 Routine service of fire protection systems and equipment | Monthly - IQP Annually - IQP | Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation
SS14 Emergency Power Systems for, or sigs relating to, a specified system and any of specified systems 1-13 | SS 14/1 Emergency power systems (for specified system) [Select] An engine alternator set for a sprinkler system pressure boost pump Uninterruptible power supply for an emergency lighting system An engine alternator set for provisions of electrical supply to passenger lifts Emergency electric supply to smoke control system | Designed and installed to NZS 6104:1981 Specification for emergency electricity supply in buildings | Application Form 27 Application for compliance schedule Full technical documentation Building Consent Form 5 SS 14/1 Emergency power systems [Select] to NZS 6104:1981 Specification for emergency electricity supply in buildings Construction documentation PS4 from Fire CPEngineer certifying system will be installed in accordance with approved consent documents | Emergency power systems require annual inspection and testing to ensure they operate as required by the performance standard, in the event that the primary power supply fails. Inspections and maintenance to NZS 6104:1981 Specification for emergency electricity supply in buildings | Monthly - IQP Annually - IQP
| SS 14/2 Signs [Select] SS1 - Automatic systems for fire suppression SS2 - Automatic or manual emergency warning systems for fire or other dangers SS3 - Electromagnetic or automatic doors or windows SS4 - Emergency lighting systems SS6 - Riser mains SS7 - Automatic back-flow preventers SS8 - Lifts, escalators, travellators, or other systems for moving people or goods within Buildings SS11 - Fume cupboards SS12 - Audio loops Security system with smoke (and/or heat) detection | Designed and installed to F8/AS1 2012 Signs Acceptable Solution | Application Form 27 Application for compliance schedule Documentation showing type and location Building Consent Form 5 SS 14/2 Signs for [Select] to F8/AS1 2012 Signs Acceptable Solution | Signage should be inspected annually in accordance with the published standard or the performance specification of the associated specified system. Inspections and maintenance procedures to ensure all signs are of correct type, present in the right locations, legible, clearly visible and unobstructed, Signs shall be refurbished before they become illegible, and shall be replaced immediately should they become illegible, and shall be replaced immediately should they be missing. | Monthly - Owner or IQP dependant on system Annually - IQP | Reference BC
SS 15 Other fire safety systems or features (systems for communicating information intended to facilitate evacuation, final exits, fire separations, signs, fire separations) | SS 15/1 Systems For Communicating Spoken Information Intended to Facilitate Evacuation [Select] A building intercom system for use by the Fire Service A public address system to facilitate staged evacuation An emergency warning intercommunications system (EWIS) | Designed and installed to NZS 4512:2010 Fire detection and alarm systems in buildings | Application Form 27 Application for compliance schedule Fire report referencing standard Building Consent Form 5 SS 15/1 Systems For Communicating Spoken Information Intended to Facilitate Evacuation [Select] to NZS 4512:2010 Fire detection and alarm systems in buildings | Systems for communicating spoken information intended to facilitate evacuation require monthly and annual inspection and testing to ensure they operate as required by the performance standard, in the event of a fire. Inspections and maintenance to NZS 4512:2010 Fire detection and alarm systems in buildings | Monthly - IQP Annually - IQP
| SS 15/2 Final Exits (doors and other exit doors in which the escape route contains one or more of the specified systems 1–6, 9 and 13) [Select] Exit doors from the building to the street Exit doors/gates at the base of an external stair/ramp Exit gate between an enclosed yard of a building and the street A door between two evacuation zones of a building with staged evacuation A door between two buildings where either building is a safe place for the adjacent building Doors – Handles/Locks | Designed and installed to C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH | Application Form 27 Application for compliance schedule Fire report and / or drawings Building Consent Form 5 SS 15/2 Final Exits [Select] to C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH | Final exits require regular inspection to ensure occupants are not prevented from leaving the building in the event of an emergency. Daily inspection, when the building is in use for crowd occupancies CS, CL, CO, CM or other building where building works is occurring that may affect an automatic door on escape route. Inspections and maintenance in accordance with MBIE Compliance Schedule Handbook for SS 15/2 | [Select] Crowd Occupancies Daily - Owner (if >1 exit & >1 level) Monthly - IQP Annually - IQP Other Occupancies Monthly - Owner Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing #number and date ) on CS
| SS 15/3 Fire Separations (protecting a means of escape which contains one or more of the specified systems 1–6, 9 and 13) [Select] Fire door forming part of a fire separation Walls forming a safe path within a building Fire rated floor/ceiling | Designed and installed to C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH | Application Form 27 Application for compliance schedule Fire report and / or drawings Building Consent Form 5 SS 15/3 Fire Separations [select] to C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH Construction documentation PS 4 fire or PS 3 passive fire protection systems Fire door certificates | Fire separations require regular inspection to ensure they prohibit the spread of fire and, in the case of fire doors; occupants are not prevented from leaving the building in the event of an emergency. Daily inspection, when the building is in use for crowd occupancies CS, CL, CO, CM or other building where building works is occurring that may affect an automatic door on escape route. Inspections and maintenance in accordance with MBIE compliance schedule handbook for SS 15/3 | Monthly - Owner 6 Monthly - IQP Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing # date ) on CS Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation or Passive fire protection specialist provides PS3 (refer building consent documents)
| SS 15/4 Signs not-illuminated (for communicating information intended to facilitate evacuation where the sign form part of a means of escape from fire which contains one or more of the specified systems 1–6, 9 and 13) | Designed and installed to F8/AS1 2012 Signs Acceptable Solution | Application Form 27 Application for compliance schedule Fire report and / or drawings Building Consent Form 5 SS 15/4 Signs not-illuminated [Select] to F8/AS1 2012 Signs Acceptable Solution | Signs require regular inspection to ensure they are displayed to facilitate evacuation in an event of an emergency. Inspections of signs not required to be illuminated to ensure they are: i) Of the correct type ii) Present and in the right locations iii) Legible | Monthly - Owner Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing number and date ) on CS
| SS 15/4 Signs Illuminated (for communicating information intended to facilitate evacuation where the sign form part of a means of escape from fire which contains one or more of the specified systems 1–6, 9 and 13) | Designed and installed to F8/AS1 2012 Signs Acceptable Solution Paragraph 4.5.1 - 4.5.3 | Application Form 27 Application for compliance schedule Product literature Building Consent Form 5 SS 15/4 Signs Illuminated [Select] to F8/AS1 2012 Signs Acceptable Solution paragraph 4.5.1 - 4.5.3 | Signs require regular inspection to ensure they are displayed to facilitate evacuation in an event of an emergency. Inspections of illuminated signs to ensure they are: i) Of the correct type ii) Present and in the right locations iii) Legible iv) Illuminated Tested to ensure they remain illuminated in the event of a failure of the main lighting supply, for the same duration as required by Clause F6. | Monthly - Owner Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing number and date ) on CS
| SS 15/4 Signs Photoluminescent signs and escape path marking | Designed and installed to F8/AS1 2012 Signs Acceptable Solution Paragraph 4.5.4 | Application Form 27 Application for compliance schedule Fire report and specific product literature Building Consent Form 5 SS 15/4 Signs Photoluminescent signs and escape path marking paragraph 4.5.4 | Signs require regular inspection to ensure they are displayed to facilitate evacuation in an event of an emergency. All products are still configured as at installation and there is no material damage to any of these products. All products are clean from general dust build up and any other specific obscuring deposits. All products are clearly visible and have not been covered up by carpet or other materials. All products mark a clear path and have not been obstructed by physical hazards such as trolleys, machinery, partitions, etc. All products can be used to provide clear escape path marking and there has been no change to the configuration of the building which renders the escape path unusable. All light required to charge the product is operation as designed at installation | Monthly - Owner Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing number and date ) on CS
| SS 15/5 Smoke Separation (that form part of the means of escape from fire which contains one or more of the specified systems 1–6, 9 and 13) [Select] Walls forming a protected path in a building Smoke resistant lift lobby A smoke stop door | Specific design to meet the requirements of C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH | Application Form 27 Application for compliance schedule Fire report Building Consent Form 5 SS 15/5 Smoke Separation [Select] to meet the requirements of C/AS2 2019 Acceptable Solution for Buildings other than Risk Group SH Construction documentation PS 4 fire protection Fire / smoke door certificates | Smoke separations require regular inspection to ensure they prohibit the passage of smoke and, in the base of smoke doors, occupants are not prevented from leaving the building in the event of an emergency. Inspections and maintenance in accordance with MBIE Compliance Schedule Handbook for SS 15/2 | [Select] Crowd Occupancies Daily - Owner (if >1 exit & >1 level) Monthly - IQP Annually - IQP Other Occupancies Monthly - Owner Annually - IQP | Reference BC document where compliance shown (e.g. As documented on fire drawing number and date ) on CS Fire Engineer supply PS4 certifying systems installed in accordance with consent documentation or Passive fire protection specialist provides PS3 (refer building consent documents) Fire / Smoke door certificates to be provided
SS16 Cable Cars | [Select] A cable car attached to or servicing a building used as a single household unit A ski chair lift which carries people in an enclosed vehicle and operates wholly or partially inside a building | Designed and installed to NZS 5270:2005 Cable cars for private residences - Design, Construction, installation and maintenance | Application Form 27 Application for compliance schedule PS1, Engineering specification and drawings referencing standard Building Consent Form 5 SS 16 Cable Cars [Select] to NZS 5270:2005 Cable cars for private residences - Design, Construction, installation and maintenance Construction documentation PS4 Structural Engineer | A cable car must be annually inspected and tested to ensure it will always operate safely. Inspections and maintenance to NZS 5270:2005 Cable cars for private residences - Design, Construction, installation and maintenance Appendix C and D | 6 Monthly - IQP Annually - IQP | Structural engineer to provide PS4, inspection records and site instructions confirmation installation in accordance with approved documents
Note on C11: Note: Standard not cited in F6 Visibility in Escape routes BCO processors to record as alternative solution
Note on C12: Note: AS/NZS 1668.1:2015 is not cited in C/AS2 and should be recorded as an alternative solution

## General information
General Information
Item | QLDC position
Definition of a crowd occupancy | Crowd small, large, open & medium as defined in the Building (Specifed Systems, Change the Use, and Earthquake-prone Buildings) Regulations 2005 - Schedule 2 Uses of all or parts of buildings
Amendments to compliance schedules | Clarification on amendments: QLDC Building Control Authority will assess if an amended compliance schedule is required when reviewing the building consent application. This includes where specified systems are installed, removed and / or alterations requiring amendments to installation, inspection and maintenance performances.